## io (hidden)
Automation Of Boiler Control
No. | Descrption | Location | PLC I/O | [5 empty] | Low | High | Input | Remark |  | Power Supply | Operation Logic / Condition | Remark / Explanation
|  |  | DI |  | DO | AI |  | AO (4-20 mA
|  |  | Feed back | Fault | Start/Stop | Current | Thermocouple
|  |  | (Run) | (Trip) | Command | Input | Input
[6 empty] | (4-20mA) | -
1 | ID FAN (Boiler Furnace Draft) | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
2 | E.F Water Pump No.1 | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
3 | E.F Water Pump No.2 | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
4 | P.FD. FAN (Boiler Steam Preesurre) | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
5 | Sec.FD. FAN | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
6 | Compressor | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
7 | Furnace Draft control | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
8 | Pendulum | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
9 | Double damper No.1 | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
10 | Double damper No.2 | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
11 | Double damper No.3 | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
12 | Dust Conveyor | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
13 | Circulation Water pump | MCC | - | 1 | - | - | - | - | - | - | Kontak 97-98 T.O.R | Alarm list trip | - | 24V From Power supply | - | Motor
14 | 2nd Low water Level (second cut off) | MCC | - | 1 | - | - | - | - | - | - | Kontak Relay X4 di MCC | Alarm list trip |  | 24V From Power supply | - | magnetic level switch
1 | Water Control (Three Element) | Instrument | - | - | 1 | 1 | - | 1 | 0% | 100% | 4-20 mA | PLC control & Monitor | AO : Mod. Valve | Loop Powered | % Low Water level to DO cut off | A1 : Level Transmitter A2 : Steam flow Transmitter A3 : Water Flow Transmitter
2 | Water flow | Instrument | - | - | - | 1 | - | - | 0 Ton | ... Ton | 4-20 mA | PLC control & Monitor | - | Loop Powered | - | Water Flow Transmitter
3 | Steam flow | Instrument | - | - | 1 | 1 | - | - | 0 Ton | ... Ton | 4-20 mA | PLC control & Monitor | - | Loop Powered | Rate flow to DO starting valve | Steam Flow Transmitter
4 | Boiler Pressure | Instrument | - | - | 1 | 1 | - | 2 | 0 Bar | 50 Bar | 4-20 mA | PLC control & Monitor | AO: 1. Damper FDF,2. Mod. sliding gate | Loop Powered | - | Pressure Transmitter
DO : Sliding on/off Solenoid
5 | Temp. Gas Duct | Instrument | - | - | - | - | 1 | - | 0°C | 500°C | TC-K Type (4-20mA) | PLC control & Monitor | - | Loop Powered | - | Temperatur Sensor
6 | Temp. Superheater | Instrument | - | - | - | - | 1 | - | 0°C | 500°C | TC-K Type (4-20mA) | PLC control & Monitor | - | Loop Powered | - | Temperatur Sensor
Paramater range lo & Hi dapat di set di HMI
|  | TOTAL | DI |  | DO | AI |  | AO
|  |  | 0 | 14 | 3 | 4 | 2 | 3
NB: | System PLC HMI Hanya di segmen intrument, namun di tambah monitoring trip motor dan cut off.
Hal ini di buat agar tidak ada memakai relay dan module tambahan dari system yang sudah ada,
sebab jika untuk monitoring & control run motor butuh relay dan module plc tambahan

## Work Flow
WORK PRINCIPLE (MBBR WWTP UTAMA) - RWW SOCI
Date of Issue : |  |  | 2024-11-15
| No. | System | Cara Pengoperasian |  | Fungsi | Cara Kerja |  | Keterangan
|  |  | Automatic | Manual
| 1 | Running Suction/Backwash MBR | √ | √ | Control | AUTO | Sistem MBR berjalan berdasarkan Level Switch : Air mencapai Level Switch → Sistem berjalan Air dibawah Level Switch → Sistem OFF Suction Pump MBR, Selenoid Valve Jalur Suction, Selenoid Valve Jalur Backwash, dan Backwash Pump MBR berjalan bergantian berdasarkan timer : a. Proses Suction : Suction Pump MBR ON selama beberapa menit → Selenoid Valve Jalur Suction OPEN → Selenoid Valve Jalur Backwash CLOSE → Backwash Pump MBR OFF (Note: lama proses suction bisa diatur pada HMI) b. Proses Backwash Setelah Suction Pump MBR OFF → Selenoid Valve Jalur Suction CLOSE → Selenoid Valve Jalur Backwash OPEN selama beberapa menit → Backwash Pump MBR ON. Jumlah Backwash Pump yang ON tergantung dari Jumlah Selenoid Valve Jalur Backwash yang terbuka / OPEN. - 1 sd 2 pcs Selenoid OPEN → 1 Pump ON - 3 sd 4 pcs Selenoid OPEN → 2 Pump ON - 5 sd 6 pcs Selenoid OPEN → 3 Pump ON - 7 sd 8 pcs Selenoid OPEN → 4 Pump ON (Note: lama proses Backwash bisa diatur pada HMI)
Jml Suction Pump MBR = 8 Unit
Jml Backwash Pump MBR = 5 Unit (Note: 4 running, 1 standby)
Jml Selenoid Valve Jalur Suction = 8 pcs
Jml Selenoid Valve Jalur Backwash = 8 pcs
Jml Level Switch = 2 pcs (1 pcs/bak)
[6 empty] | MANUAL | a. Proses Suction secara Manual : Suction Pump MBR dan Selenoid Valve Jalur Suction dioperasikan menggunakan Tombol ON/OFF MBR Suction 1 - 8. (Note: 1 tombol terintegrasi untuk Pump dan Selenoid) b. Proses Backwash secara Manual : Backwash pump MBR dioperasikan menggunakan Tombol ON/OFF MBR Backwash Pump 1 - 5. Selenoid Valve Jalur Backwash dibuka/tutup menggunakan Tombol ON/OFF SV MBR Backwash 1 - 8. (Note: Tombol untuk Pump dan Selenoid dibedakan)
| 2 | Running Pompa Sirkulasi | √ | √ | Control | AUTO | pompa berjalan berdasarkan Level Switch : Air mencapai Level Switch → Pompa ON Air dibawah Level Switch → Pompa OFF
Jml Circulation Pump MBR = 2 Unit
Jml Level Switch = 2 pcs (1 pcs/bak) (Note: Item yang sama pada Poin 1)
[6 empty] | MANUAL | Pompa dioperasikan menggunakan Tombol ON/OFF Circulation MBR 1 - 2